## Slide 1
IEC 61158 / IEC 61784
#1
Industrial Ethernet
in Europe
PROFINET
Protocol Explained
Industrial Ethernet for Factory Automation
Team:
Rionela Kovaci
Christian Percival
Mohamed Abdo
Supervisor: Prof. Dr.-Ing. Ali Hayek

## Slide 2
Motivation — Why PROFINET?
From home networks to factory-floor real-time communication
The Problem with Regular Ethernet in Factories:
Designed for best-effort delivery, no timing guarantees
100 ms delay is fine for streaming video, catastrophic for a robot arm
TCP/IP stack adds unpredictable latency
Why Factories Need Something Different:
Machines or CNC needs a response < 1 ms
One missed signal = broken part or safety risk
1000s of devices must be synchronized, not just connected

## Slide 3
Motivation — Why PROFINET?
From home networks to factory-floor real-time communication
PROFINET solves this by:
Bypassing the TCP/IP stack entirely for time-critical data
Guaranteeing cycle times down to 125 µs
Running safety, motion, and Errors diagnostics on the same cable

## Slide 4
WHAT IS PROFINET?
PROFINET is an open Industrial Ethernet standard designed to exchange data between controllers and field devices in automation systems. standardized under IEC 61158 and IEC 61784, with support for real-time and isochronous real-time communication, integrated with PROFIsafe.
SAFE
Source: Analysis of PROFINET IO Communication Protocol | IEEE Conference Publication | IEEE Xplore

## Slide 5
Can you build a PROFINET protocol prototype in the lab?

## Slide 6
HOW PROFINET WORKS
PLC
(IO Controller)
Siemens S7-1500/1200, Beckhoff CX,
Rockwell 5380
Ethernet
Switch
Must support PROFINET DCP, LLDP & SNMP. RT
HMI
Human Machine Interface
(IO Supervisor)
shark wire
Cyclic IO Data (RT frames, EtherType 0x8892)
PROFINET - Wireshark Wiki

## Slide 7
BUILDING A PROFINET NETWORK — 💻 SOFTWARE
Engineering Tool (PLC IDE)
Siemens TIA Portal (most common), CODESYS, Rockwell Studio 5000, Phoenix PLCnext Engineer — used to configure PROFINET network and program PLC logic
GSDML Files (per device)
XML-based General Station Description files — supplied by each device vendor. Import into the engineering tool to auto-configure IO data mappings and parameters

## Slide 8
BUILDING A PROFINET NETWORK — 💻 SOFTWARE
Network Commissioning Tool
Siemens PRONETA (free), NetScan tools — scans the PROFINET network, assigns IP/device names, shows topology and device status without requiring a running PLC
Diagnostics Software
PROFINET-aware network analyzers (Wireshark + PROFINET dissector, Softing, Procentec ComBricks) for live frame capture, alarm analysis, and performance monitoring
Analysis of PROFINET IO Security Extensions on Wireshark | IEEE Conference Publication | IEEE Xplore

## Slide 9
PROFINET raspberry pi Prototype

## Slide 10
Christian‘s Part

## Slide 11
3 COMMUNICATION CHANNELS & types
TCP/IP
Cycle: ~100 ms
Non-Real-Time Channel
Used for configuration, parameterization, diagnostics, and IT integration. Travels through the full TCP/IP stack. Not suitable for time-critical tasks.
▸ Device configuration
▸ SNMP diagnostics
▸ OPC UA, HTTP, MQTT coexistence
RT
Cycle: 1–10 ms
Real-Time Channel
Cyclic IO data exchange using Layer 2 Ethernet frames (EtherType 0x8892). Bypasses the TCP/IP stack entirely for low latency.
▸ Sensor/actuator IO
▸ Valve & motor control
▸ Discrete IO monitoring
IRT
Cycle: < 1 ms
Isochronous Real-Time
Synchronized time-slot communication with hardware-level scheduling. Requires special IRT-capable switches. Reserved for demanding motion control.
▸ CNC / servo drives
▸ Multi-axis coordination
▸ High-speed robotics

## Slide 13
PROFIsafe — FUNCTIONAL SAFETY OVER PROFINET
PROFIsafe is a safety communication profile (IEC 61784-3-3) built on top of PROFINET using the "Black Channel" principle — it adds its own error-detection layer above the standard network, so safety-critical signals (E-Stop, light curtains, safety doors) travel on the same cable as regular automation data without requiring separate wiring.
BLACK CHANNEL PRINCIPLE
Safety Function (F-CPU ↔ F-Device)
PROFIsafe Layer (CRC + Consecutive No.)
PROFINET RT (Black Channel – untouched)
Ethernet Physical (Cat 5e / Cat 6)
Safety Level:
Up to SIL 3 (IEC 61508)
PL e / Cat 4 (ISO 13849)
Certified By:
TÜV SÜD + IFA (Germany)
Standard:
IEC 61784-3-3 (since 2007)
Key Mechanism:
CRC checksum + Consecutive Number + Watchdog Timer
Use Cases:
E-Stop, light curtains, safety doors, safe speed monitoring
⚠ PROFIsafe does NOT replace a risk assessment — it provides the communication infrastructure for safety functions already designed per ISO 13849 / IEC 62061.

## Slide 14
PROFIsafe

## Slide 15
Christian‘s Part

## Slide 16
Rio‘s Part

## Slide 17
PROFINET HARDWARE CHIPS — IMPLEMENTATION APPROACHES
Building a PROFINET IO Device requires dedicated hardware to handle real-time Ethernet frames. Three main implementation paths exist — each with different trade-offs in cost, performance, flexibility, and time-to-market.
01
Dedicated
ASIC / SoC
✔ Advantages
+ Best RT/IRT performance
+ Low CPU load
+ Smallest footprint
+ Low power
✖ Limitations
– Fixed protocol
– High NRE cost
– Long design cycle
Siemens ERTEC 200P
Hilscher netX 90
Renesas R-IN32M3
02
General MCU
+ PRU / Soft-IP
✔ Advantages
+ Multi-protocol capable
+ Lower BOM cost
+ Software-upgradeable
+ Large ecosystem
✖ Limitations
– More SW effort
– Limited IRT support
– Higher CPU overhead
TI AM64x (PRU-ICSSG)
TI AMIC110
NXP i.MX RT
03
FPGA-based
Implementation
✔ Advantages
+ Maximum flexibility
+ IRT capable
+ Custom logic possible
+ Multi-protocol
✖ Limitations
– Highest cost
– Complex design
– Large power budget
Intel/Altera (EtherBrick)
Xilinx Artix-7
(with 3rd-party IP cores)
Note: 'Conformance Classes' A (RT only), B (RT+topology), C (IRT) determine which chip category is required.

## Slide 18
MCU-BASED APPROACHES — Renesas R-IN32 & Texas Instruments Sitara
🇯🇵 RENESAS — R-IN32 Family
R-IN32M3
ARM Cortex-M3 + R-IN Engine
PROFINET RT, EtherNet/IP, EtherCAT
2-port 100 Mbps switch, multiprotocol
🇺🇸 TEXAS INSTRUMENTS — Sitara / PRU-ICSS
AMIC110 (Sitara)
ARM Cortex-A8, ~$4/unit
PRU-ICSS subsystem for protocol offload
PROFINET RT, EtherNet/IP, EtherCAT from same HW

## Slide 19
MCU-BASED APPROACHES — Renesas R-IN32 & Texas Instruments Sitara
🇯🇵 RENESAS — R-IN32 Family

## Slide 20
What makes these Chips different in profinet fast timming?

## Slide 21
PROFINET APPLICATION AREAS
🏭
Discrete Manufacturing
Assembly lines, conveyor systems, pick-and-place, welding cells
⚙️
Machine Tools / CNC
Multi-axis servo coordination via PROFIdrive, <1 ms IRT cycles
🤖
Robotics
ABB, FANUC, KUKA — all support PROFINET natively for arm control
🏗️
Automotive
Body-in-white, paint, powertrain assembly; 100% PROFINET lines at VW, BMW
💊
Pharma & Food
PROFIsafe ensures SIL-rated interlocks for FDA/GMP-compliant lines
🌊
Water / Oil & Gas
Remote pump/valve control over long distances; PROFIBUS proxy integration
🔋
Energy / Utilities
Substation automation, wind turbines, solar plant SCADA networks
🏢
Building Automation
HVAC, access control, fire suppression with OPC UA coexistence

## Slide 22
PROFINET vs. INDUSTRIAL ETHERNET STANDARDS
Feature
PROFINET
+PROFIsafe
EtherNet/IP
+CIP Safety
EtherCAT
+FSoE
Modbus TCP
CC-Link IE
POWERLINK
Standard
IEC 61158/61784
ODVA / IEC 61784
ETG / IEC 61158
Open / Modicon
CLPA / IEC 61784
Ethernet POWERLINK
Cycle Time
< 1 ms (IRT)
1–10 ms
< 0.1 ms
10–100 ms
< 1 ms
< 1 ms
Safety Profile
PROFIsafe SIL 3
CIP Safety SIL 3
FSoE SIL 3
✗ None
CC-Link Safety
openSAFETY SIL 3
Market Focus
Europe / Global
North America
Motion Control
Universal/Legacy
Asia (Mitsubishi)
European OEMs
Std. Ethernet HW
✔ Yes (RT)
✗ IRT needs special SW
✔ Yes
✗ Needs ASIC
✔ Yes
✔ Yes (1 Gbps)
✔ Yes
Topology
Star/Ring/Line
Star/Ring
Line/Ring
Star
Star/Ring/Line
Line/Ring
Vendor Lock
Open, PI governed
Open, ODVA governed
Open, ETG governed
Open, Modicon
Mitsubishi-led
Open, B&R/Ethernet

## Slide 23
Rio‘s Part

## Slide 24
Christian‘s Part

## Slide 25
PROFINET STANDARDS refrences
IEC 61158
Industrial communication networks – Fieldbus specifications. Defines PROFINET physical layer, data link layer, and application layer protocol.
IEC 61784
Industrial communication networks – Profiles. Defines communication profiles including CPF 3 (PROFINET), specifying device behavior and interoperability.
IEC 61784-1
Communication Profiles
Cyclic and acyclic data exchange profiles for industrial fieldbuses
IEC 61784-2
Real-Time Networks
RT and IRT performance requirements for industrial Ethernet
IEC 61784-3-3
PROFIsafe
Functional safety communication profile (SIL 3 / PL e)
IEC 61784-5-3
Installation Guide
Cabling, connectors, and infrastructure for PROFINET networks
IEEE 802.3
Ethernet Base
Standard Ethernet physical/link layer PROFINET runs on top of
ISO 13849 / IEC 61508
Safety Basis
Functional safety standards PROFIsafe is built upon (PLe / SIL 3)

## Slide 26
Refences
Thank you
References
[1]
S. Vitturi et al., "Ethernet-based real-time communications with PROFINET IO," IEEE IECON, 2009. DOI: 10.1109/IECON.2009.5414860
[2]
L. Dürkop et al., "Isochronous Real-Time in PROFINET," IEEE INDIN, 2014. DOI: 10.1109/INDIN.2014.6945612
[3]
P. Moraes et al., "Real-Time Ethernet in Industrial Automation," IEEE ETFA, 2010. DOI: 10.1109/ETFA.2010.5641343
[4]
R. Pigan & M. Metter, Automating with PROFINET, 2nd ed. Publicis, 2008. ISBN 978-3-895-78348-1
[5]
PI (PROFIBUS & PROFINET Int.), "PROFINET System Description," Order No. 4.132, 2022. profibus.com
[6]
IEC 61158 — Industrial communication networks – Fieldbus specifications (PROFINET). IEC, Geneva.
[7]
IEC 61784-3-3 — PROFIsafe: Functional Safety Fieldbuses, Ed. 3.0, 2021. IEC, Geneva.
[8]
Siemens AG, ERTEC 200P Product Brief, 6GK1184-0BB01, 2023. industry.siemens.com
[9]
Hilscher GmbH, netX 90 Datasheet Rev. 2, 2019. hilscher.com
[10]
Texas Instruments, AM64x Sitara Processors Datasheet (SPRSP28), 2022. ti.com
PROFINET
Protocol Explained
Thank You
profinet.com
profibus.com
ieeexplore.ieee.org
hilscher.com/netx
renesas.com/r-in
ti.com/sitara
Questions & Live Demo